## Details
Date | NEA Curtailed Energy | NEA trip loss time (min) | No of Trippings | Loss Time (Min) | Loss Time for Unit I (Min) | Loss Time for Unit II(Min) | Energy loss due to Line Tripping | Energy loss due to Other reasons | Total energy loss | Reason for Tripping
2023-03-16 | 10.65 | 336 |  |  |  |  | 0 | 0 | 0
2023-03-17 | [6 empty] | 0 | 0 | 0
2023-03-18 | 9 | 180 |  |  |  |  | 0 | 0 | 0
2023-03-19 | 0 | [5 empty] | 0 | 0 | 0
2023-03-20 | 6.65 | 133 |  |  |  |  | 0 | 0 | 0
2023-03-21 | 1.9667 | 118 | 1 |  | 182 | 182 | 0 | 10.8168 | 10.8168 | SST Panel change
2023-03-22 | 0 |  | 1 |  | 18 | 18 | 0 | 0 | 0 | For Wire correction in tx line
2023-03-23 | 0
2023-03-24 | 0.71667 | 43
2023-03-25 | 0
2023-03-26 | 0
2023-03-27 | 0
2023-03-28 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0
2023-03-29 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0
2023-03-30 | 0 |  | 1 |  | 11 | 11 | 0 | 0 | 0
2023-03-31 | 0 | [5 empty] | 0 | 0 | 0
2023-04-01 | 0
2023-04-02 | 0
2023-04-03
2023-04-04
2023-04-05
2023-04-06
2023-04-07
2023-04-08
2023-04-09
2023-04-10
2023-04-11
2023-04-12 | [6 empty] | 0 | 0 | 0
2023-04-13 | [6 empty] | 0 | 0 | 0
2023-04-14 | [6 empty] | 0 | 0 | 0
2023-04-15 | [5 empty] | 0 | 0 | 0 | 0
2023-04-16 | [5 empty] | 0 | 0 | 0 | 0
2023-04-17 | [5 empty] | 0 | 0 | 0 | 0
2023-04-18 |  |  | 2 | 9 | [5 empty] | Grid Faults
2023-04-19 |  |  | 3 | 24 | [5 empty] | Grid Faults
2023-04-20 |  |  | 1 | 15 | [5 empty] | Grid Faults
2023-04-21 |  |  | 2 | 27 | [5 empty] | Grid Faults
2023-04-22 |  |  | 3 | 25 | [5 empty] | Grid Faults
2023-04-23 |  |  | 1 | 7 | [5 empty] | Grid Faults
2023-04-24 |  |  | 0 | 0 | [5 empty] | Grid Faults
2023-04-25 |  |  | 2 | 0 | [5 empty] | Grid Faults
2023-04-26 |  |  | 3 | 0 | [5 empty] | Grid Faults
2023-04-27 |  |  | 1 | 3 | [5 empty] | Grid Faults
2023-04-28 |  |  | 1 | 2 | [5 empty] | Grid Faults
2023-04-29 |  |  | 3 | 14 | [5 empty] | Grid Faults
2023-04-30 |  |  | 1 | 3 | [5 empty] | Grid Faults
2023-05-01 |  |  | 2 | 13 | [5 empty] | Grid Faults
2023-05-02 |  |  | 2 | 17 | 2 | 0.64896 | 0.64896 | 0 | 0.64896 | Grid Faults
2023-05-03 | [7 empty] | 0 | 0 | Grid Faults
2023-05-04 | [7 empty] | 0 | 0 | Grid Faults
2023-05-05 | [7 empty] | 0 | 0 | Grid Faults
2023-05-06 |  |  | 1 | 8 |  |  |  | 0 | 0 | Grid Faults
2023-05-07 |  |  | 1 | 8 |  |  |  | 0 | 0 | Grid Faults
2023-05-08 | [7 empty] | 0 | 0 | Grid Faults
2023-05-09 |  |  | 2 | 25 |  | 1.6303 | 1.6303 | 0 | 1.6303 | Grid Faults
2023-05-10 |  |  | 0 | 0 | [5 empty] | Grid Faults
2023-05-11 |  |  | 0 | 0 | [5 empty] | Grid Faults
2023-05-12 |  |  | 1 | 0 | [5 empty] | Grid Faults
2023-05-13 |  |  | 3 | 14 |  | 0.26012 | 0.26012 | 0 | 0.26012 | Grid Faults
2023-05-14 |  |  | 2 | 14 |  | 0.29955 | 0.29955 | 0 | 0.29955 | Grid Faults
2023-05-15 |  |  | 3 | 35 |  | 3.6012 | 3.6012 | 0 | 3.6012 | Grid Faults
2023-05-16 | [6 empty] | 0 | 0 | 0
2023-05-17 |  |  | 1 | 7 |  |  | 1.1001 | 0 | 1.1001
2023-05-18 |  |  | 5 | 87 |  |  | 14.5075 | 0 | 14.5075 | Shutdown for Txline repair and Grid Faults
2023-05-19 |  |  | 0 | 0 |  |  | 0 | 0 | 0
2023-05-20 |  |  | 1 | 8 |  |  | 1.2956 | 0 | 1.2956 | For changing sensor cable
2023-05-21 |  |  | 1 | 8 |  |  | 1.1727 | 0 | 1.1727 | Grid Faults
2023-05-22 |  |  | 0 | 0 |  |  | 0 | 0 | 0
2023-05-23 |  |  | 4 | 36 |  |  | 5.9985 | 0 | 5.9985
2023-05-24 | 9.3917 |  | 6 | 169.8 |  |  | 26.5527 | 0 | 26.5527 | Grid Faults + 33 kV faults+ Dispatch
2023-05-25 | 34.26 |  | 3 | 19 |  |  | 2.6826 | 0 | 2.6826 | Grid Faults + 33 kV faults+ Dispatch
2023-05-26 |  |  | 1 | 12 |  |  | 2.0332 | 0 | 2.0332 | Grid Faults
2023-05-27 |  |  | 8 | 117 |  |  | 19.4946 | 0 | 19.4946 | Grid Faults/Powerhouse faults
2023-05-28 |  |  | 5 | 133 |  |  | 19.9166 | 0 | 19.9166 | Grid Faults/Powerhouse faults
2023-05-29
2023-05-30 |  |  | 3 | 32 |  |  | 5.0046 | 0 | 5.0046 | Grid Faults/Powerhouse faults
2023-05-31 |  |  | 5 | 54 |  |  | 8.7847 |  | 8.7847 | Grid Faults/Powerhouse faults
2023-06-01 |  |  | 2 | 21 |  |  | 3.0108 |  | 3.0108 | Grid Faults/Powerhouse faults
2023-06-02 |  |  | 3 | 97 |  |  | 14.2789 |  | 14.2789 | Grid Faults/Powerhouse faults
2023-06-03 |  |  | 2 | 18 |  |  | 2.3168 |  | 2.3168 | Grid Faults/Powerhouse faults
2023-06-04 |  |  | 3 | 25 |  |  | 3.3297 |  | 3.3297 | Grid Faults/Powerhouse faults
2023-06-05 |  |  | 4 | 49 |  |  | 7.7453 |  | 7.7453 | Grid Faults/Powerhouse faults
2023-06-06 |  |  | 5 | 39 |  |  | 5.5039 |  | 5.5039 | Grid Faults/Powerhouse faults
2023-06-07 |  |  | 0 | 0 |  |  | 0 |  | 0 | Grid Faults/Powerhouse faults
2023-06-08 |  |  | 1 | 13 |  |  | 1.6561 |  | 1.6561 | Grid Faults/Powerhouse faults
2023-06-09 |  |  | 4 | 61 |  |  | 9.0965 |  | 9.0965 | Grid Faults/Powerhouse faults
2023-06-10 |  |  | 2 | 26 |  |  | 3.6797 |  | 3.6797 | Grid Faults/Powerhouse faults
2023-06-11 |  |  | 3 | 87 |  |  | 13.1906 |  | 13.1906 | Grid Faults/Powerhouse faults
2023-06-12 |  |  | 3 | 9 |  |  | 1.436 |  | 1.436 | Grid Faults/Powerhouse faults
2023-06-13 |  |  | 12 | 74 |  |  | 12.3266 |  | 12.3266 | Grid Faults/Powerhouse faults
2023-06-14 | [6 empty] | 0 |  | 0
2023-06-15 |  |  | 1 | 1032 |  |  | 170.4065 |  | 170.4065 | Tx line Line damaged by rockfall
2023-06-16 |  |  | 2 | 475 |  |  | 79.959 |  | 79.959 | Grid Faults/Powerhouse faults
2023-06-17 |  |  | 3 | 994 |  |  | 168.8953 | 0 | 168.8953 | Grid Faults/Powerhouse faults
2023-06-18 |  |  | 13 | 223 |  |  | 37.5001 | 0 | 37.5001 | Grid Faults/Powerhouse faults
2023-06-19 |  |  | 6 | 37 |  |  | 6.1252 | 0 | 6.1252 | Grid Faults/Powerhouse faults
2023-06-20 |  |  | 5 | 68 |  |  | 11.3269 | 0 | 11.3269 | Grid Faults/Powerhouse faults
2023-06-21 | 188 |  | 12 | 84 |  |  | 14.1636 | 0 | 14.1636 | Grid Faults/Powerhouse faults
2023-06-22 |  |  | 14 | 95 |  |  | 15.8566 | 0 | 15.8566 | Grid Faults/Powerhouse faults
2023-06-23 |  |  | 4 | 80 |  |  | 13.0071 | 0 | 13.0071 | Grid Faults/Powerhouse faults
2023-06-24 |  |  | 1 | 10 |  |  | 1.6701 | 0 | 1.6701 | Grid Faults/Powerhouse faults
2023-06-25 |  |  | 6 | 341 |  |  | 56.8437 | 0 | 56.8437 | Grid Faults/Powerhouse faults/Tx line Faults
2023-06-26 |  |  | 1 | 1440 |  |  | 240 | 0 | 240 | Transmission Line Faults
2023-06-27 |  |  | 1 | 1440 |  |  | 240 | 0 | 240 | Transmission Line Faults
2023-06-28 |  |  | 1 | 1382 |  |  | 216.2115 | 0 | 216.2115 | Transmission Line Faults
2023-06-29 |  |  | 11 | 408 |  |  | 66.7025 | 0 | 66.7025 | Grid Faults/Powerhouse faults/Station Transformer Faults
2023-06-30 |  |  | 5 | 72 |  |  | 11.9518 | 0 | 11.9518 | Grid Faults/Powerhouse faults
2023-07-01 | 30 |  | 4 | 62 |  |  | 9.9829 | 0 | 9.9829 | Grid Faults/Powerhouse faults
2023-07-02 |  |  | 2 | 22 |  |  | 3.6548 | 0 | 3.6548 | Grid Faults/Powerhouse faults
2023-07-03 |  |  | 3 | 81 |  |  | 13.367 | 0 | 13.367 | Grid Faults/Powerhouse faults
2023-07-04 |  |  | 1 | 17 |  |  | 2.8247 | 0 | 2.8247 | Grid Faults/Powerhouse faults
2023-07-05 |  |  | 2 | 21 |  |  | 3.48 | 0 | 3.48 | Grid Faults/Powerhouse faults
2023-07-06 |  |  | 2 | 3 |  |  | 0.49502 | 0 | 0.49502 | Powerhouse faults
2023-07-07 |  |  | 2 | 11 |  |  | 1.8239 | 0 | 1.8239
2023-07-08 |  |  | 0 | 0 |  |  | 0 | 0 | 0
2023-07-09 |  |  | 4 | 222 |  |  | 36.5935 | 0 | 36.5935 | 132 kV tx line 2nd circuit charging
2023-07-10 |  |  | 7 | 427 |  |  | 72.391 | 0 | 72.391 | 132 kV tx line 2nd circuit charging
2023-07-11 |  |  | 3 | 809 |  |  | 134.2722 | 0 | 134.2722 | 33 kV line issue/132 kV charging
2023-07-12 |  |  | 3 | 30 |  |  | 5.0023 | 0 | 5.0023 | Grid Faults/Powerhouse faults
2023-07-13 | [6 empty] | 0 | 0 | 0
2023-07-14 |  |  | 1 | 200 |  |  | 33.1806 | 0 | 33.1806 | Penstock repair and optical cable damage
2023-07-15 |  |  | 1 | 1439.999 |  |  | 240 | 0 | 240
2023-07-16 |  |  | 1 | 1439.999 |  |  | 240 | 0 | 240
2023-07-17 |  |  | 1 | 1439.999 |  |  | 240 | 0 | 240
2023-07-18 | [6 empty] | 240 | 0 | 240 | Penstock Repair
2023-07-19 | [6 empty] | 240 | 0 | 240 | Penstock Repair
2023-07-20 | [6 empty] | 240 | 0 | 240 | Penstock Repair
2023-07-21 | [6 empty] | 240 | 0 | 240 | Penstock Repair
2023-07-22 | [6 empty] | 240 | 0 | 240 | Penstock Repair
2023-07-23 | [6 empty] | 240 | 0 | 240 | Penstock Repair
2023-07-24 | [6 empty] | 240 | 0 | 240 | Penstock Repair
2023-07-25 | [6 empty] | 240 | 0 | 240 | Penstock Repair
2023-07-26 | [6 empty] | 240 | 0 | 240 | Penstock Repair
2023-07-27 | [6 empty] | 240 | 0 | 240 | Penstock Repair
2023-07-28 | [6 empty] | 240 | 0 | 240 | Penstock Repair
2023-07-29 | [6 empty] | 240 | 0 | 240 | Penstock Repair
2023-07-30 | [6 empty] | 240 | 0 | 240 | Penstock Repair
2023-07-31 | [6 empty] | 240 | 0 | 240 | Penstock Repair
2023-08-01 | [6 empty] | 240 | 0 | 240 | Penstock Repair
2023-08-02 | [6 empty] | 240 | 0 | 240 | Penstock Repair
2023-08-03 | [6 empty] | 240 | 0 | 240 | Penstock Repair
2023-08-04 | [6 empty] | 240 | 0 | 240 | Penstock Repair
2023-08-05 | [6 empty] | 240 | 0 | 240 | Running plant in 6.5 MW only
2023-08-06 | [6 empty] | 0 | 0 | 0 | Running plant in 7.5 MW only
2023-08-07 |  |  | 2 | 1 |  |  | 0.12437 | 0.87059 | 0.99496 | Running plant in 7.5 MW only/Grid Faults/ Trip for checking pressure
2023-08-08 |  |  | 2 | 16 |  |  | 2.1389 | 0 | 2.1389 | Running plant in 8 MW only/Grid Faults
2023-08-09 |  |  | 5 | 47 |  |  | 6.3046 | 0 | 6.3046 | Running plant in 8.25 MW only/Grid Faults
2023-08-10 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | Running plant in 8.5 MW only
2023-08-11 |  |  | 2 | 120 |  |  | 16.8446 | 0 | 16.8446 | Running plant in 8.5 MW only
2023-08-12 | [6 empty] | 0 | 0 | 0 | Running plant in 8.75 MW only
2023-08-13 |  |  | 3 | 28 |  |  | 4.1282 | 0 | 4.1282 | Running plant in 9.00 MW only/Sensor trip
2023-08-14 |  |  | 3 | 20 |  |  | 2.9557 | 0 | 2.9557 | Running plant in 9.00 MW only/Sensor trip
2023-08-15 |  |  | 0 |  |  |  | 0 | 0 | 0
2023-08-16 |  |  | 2 | 15 |  |  | 2.2878 | 0 | 2.2878 | Running plant in 9.00 MW only/Grid faults
2023-08-17 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | Running plant in 9.50 MW only
2023-08-18 |  |  | 1 | 11 |  |  | 1.7606 | 0 | 1.7606 | Running plant in 9.750 MW only and water level sensor issue due to power cut
2023-08-19 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0
2023-08-20 |  |  | 3 | 23 |  | 0 | 3.7823 | 0 | 3.7823 | Generation more than 10 MW
2023-08-21 |  |  | 3 | 53 |  | 1002 | 8.9074 | 83.5 | 92.4074 | Unit I stopped due to spear valve issue
2023-08-22 |  |  | 1 | 6 |  | 498 | 1.01 | 41.5 | 42.51 | Only Unit I tripped
2023-08-23 |  |  | 2 | 32 |  | 0 | 5.1926 | 0 | 5.1926 | Trip from powerhouse
2023-08-24 |  |  | 4 |  | 323 | 408 | 0 | 56.4783 | 56.4783 | Trip from powerhouse for DDLO, Unit II repair and intake cleaning for removing logs and penstock pipe damage
2023-08-25 |  |  | 1 | 0 | 1440 | 1440 | 0 | 240 | 240 | Penstock pipe damage repair
2023-08-26 |  |  | 1 | 0 | 1440 | 1440 | 0 | 240 | 240 | Penstock pipe damage repair
2023-08-27 |  |  | 1 | 0 | 1440 | 1440 | 0 | 240 | 240 | Water filling in penstock pipe
2023-08-28 |  |  | 2 | 17 | 410 | 410 | 2.8167 | 67.9314 | 70.7481 | Water filling in penstock pipe half day
2023-08-29 |  |  | 3 | 27 |  |  | 4.5036 | 0 | 4.5036 | Grid faults
2023-08-30 | 9.4667 |  | 4 | 35 |  |  | 5.6265 | 0 | 5.6265 | Grid faults / LDC dispatch instruction to lower power to 9 MW
2023-08-31 |  |  | 8 | 54 | 0 |  | 8.7992 | 0 | 8.7992 | Grid faults
2023-09-01 |  |  | 2 | 13 |  |  | 1.9881 | 0 | 1.9881 | Grid faults / LDC dispatch instruction to lower power to 9 MW
2023-09-02 |  |  | 2 | 16 | 10 |  | 2.51 | 0.78438 | 3.2944 | Grid faults / LDC dispatch instruction to lower power to 9 MW
2023-09-03 |  |  | 1 | 5 |  | 4 | 0.85625 | 0.3425 | 1.1987 | Plant running at 10.5 MW
2023-09-04 |  |  | 1 | 7 | 3 | 0 | 1.205 | 0.2582 | 1.4632 | Plant running at 10.5 MW
2023-09-05 | 16.57 |  | 1 | 0 |  | 0 | 0 | 0 | 0 | Plant running at 10.5 MW
2023-09-06 |  |  | 1 | 0 | 3 | 0 | 0 | 0.25974 | 0.25974 | Plant running at 10.5 MW
2023-09-07 |  |  | 1 | 5 | 0 | 0 | 0.86611 | 0 | 0.86611 | Plant running at 10.5 MW
2023-09-08 |  |  | 5 | 60 | 0 | 0 | 10.4564 | 0 | 10.4564 | Plant running at 10.5 MW
2023-09-09 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Plant running at 10.5 MW
2023-09-10 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Plant running at 10.5 MW
2023-09-11 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Plant running at 10.5 MW
2023-09-12 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Plant running at 10.5 MW
2023-09-13 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Plant running at 10.5 MW
2023-09-14 |  |  | 1 | 21 | 0 | 0 | 3.6496 | 0 | 3.6496 | Plant running at 10.5 MW
2023-09-15 |  |  | 1 |  | 8 | 15 | 0 | 1.9876 | 1.9876 | Plant running at 10.5 MW
2023-09-16 |  |  | 1 | 5 |  |  | 0.86128 | 0 | 0.86128 | Plant running at 10.5 MW
2023-09-17 | [6 empty] | 0 | 0 | 0 | Plant running at 10.5 MW
2023-09-18 | [6 empty] | 0 | 0 | 0 | Plant running at 10.5 MW
2023-09-19 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0
2023-09-20 |  |  | 3 | 23 |  | 0 | 3.9502 | 0 | 3.9502 | Grid Faults
2023-09-21 |  |  | 1 |  | 156 | 156 | 0 | 27.1993 | 27.1993 | Station transformer fault
2023-09-22 |  |  | 1 |  | 30 | 30 | 0 | 5.1622 | 5.1622 | Optical cable damage
2023-09-23 |  |  | 2 | 14 |  |  | 2.4297 | 0 | 2.4297 | Grid Faults
2023-09-24 |  |  | 0 |  |  |  | 0 | 0 | 0
2023-09-25 |  |  | 2 | 24 |  |  | 4.1374 | 0 | 4.1374 | Grid Faults
2023-09-26 |  |  | 0 | 0 |  |  | 0 | 0 | 0
2023-09-27 |  |  | 0 | 0 |  |  | 0 | 0 | 0
2023-09-28 |  |  | 0 | 0 |  |  | 0 | 0 | 0
2023-09-29 |  |  | 0 | 0 |  |  | 0 | 0 | 0
2023-09-30 |  |  | 2 | 31 |  | 29 | 5.3814 | 2.5171 | 7.8985 | Grid Faults
2023-10-01 |  |  | 1 | 31 |  | 96 | 5.407 | 8.3721 | 13.7791 | Grid Faults and maintainance works, SST transformer damage, unit I couldn't operate
2023-10-02 |  |  | 2 | 220 | 330 |  | 38.3578 | 27.5 | 65.8578 | Grid Faults and maintainance works, SST transformer damage, unit I couldn't operate
2023-10-03 |  |  | 2 | 250 |  |  | 43.3475 | 0 | 43.3475 | Grid Faults for 132 kV repair
2023-10-04 |  |  | 1 | 7 |  |  | 1.2189 | 0 | 1.2189 | Earthquake
2023-10-05 |  |  | 1 | 5 |  |  | 0.86751 | 0 | 0.86751 | Grid Faults
2023-10-06 |  |  | 1 | 5 |  |  | 0.86773 | 0 | 0.86773 | Grid Faults
2023-10-07 |  |  | 1 | 5 |  |  | 0.86747 | 0 | 0.86747 | Grid Faults
2023-10-08 |  |  | 1 | 39 |  |  | 6.773 | 0 | 6.773 | 50 kVA station transformer installed
2023-10-09 | [6 empty] | 0 | 0 | 0
2023-10-10 | [6 empty] | 0 | 0 | 0
2023-10-11 | [6 empty] | 0 | 0 | 0
2023-10-12 | [6 empty] | 0 | 0 | 0
2023-10-13 | [6 empty] | 0 | 0 | 0
2023-10-14 | [6 empty] | 0 | 0 | 0
2023-10-15 | [6 empty] | 0 | 0 | 0
2023-10-16 |  |  | 1 | 6 |  |  | 1.0409 | 0 | 1.0409
2023-10-17 |  |  | 2 | 26 |  |  | 4.5221 | 0 | 4.5221
2023-10-18 | [6 empty] | 0 | 0 | 0
2023-10-19 | [6 empty] | 0 | 0 | 0
2023-10-20 | [6 empty] | 0 | 0 | 0
2023-10-21 |  |  | 3 | 60 |  |  | 10.4905 | 0 | 10.4905 | Grid Faults
2023-10-22 |  |  | 2 | 16 |  |  | 2.7659 | 0 | 2.7659 | Grid Faults
2023-10-23 |  |  | 2 | 22 |  |  | 3.8041 | 0 | 3.8041 | Grid Faults
2023-10-24 | [6 empty] | 0 | 0 | 0
2023-10-25 |  |  | 1 | 7 |  |  | 1.1735 | 0 | 1.1735 | Grid Faults
2023-10-26 |  |  | 1 | 26 |  |  | 4.26 | 0 | 4.26 | Grid Faults
2023-10-27 | [6 empty] | 0 | 0 | 0
2023-10-28 | [6 empty] | 0 | 0 | 0
2023-10-29 | [6 empty] | 0 | 0 | 0
2023-10-30 | [6 empty] | 0 | 0 | 0
2023-10-31 | [6 empty] | 0 | 0 | 0
2023-11-01 | [6 empty] | 0 | 0 | 0
2023-11-02 |  |  | 1 | 10 |  |  | 1.4512 | 0 | 1.4512
2023-11-03 | [6 empty] | 0 | 0 | 0
2023-11-04 |  |  | 1 | 6 |  |  | 0.83285 | 0 | 0.83285
2023-11-05 | [6 empty] | 0 | 0 | 0
2023-11-06 | [6 empty] | 0 | 0 | 0
2023-11-07 | [6 empty] | 0 | 0 | 0
2023-11-08 |  |  | 1 | 24 |  |  | 3.0741 | 0 | 3.0741 | Waterl level sensor off due to power out
2023-11-09 | [6 empty] | 0 | 0 | 0
2023-11-10 |  |  | 2 | 26 |  |  | 3.3255 | 0 | 3.3255 | Waterl level sensor off due to power out
2023-11-11 |  |  | 1 | 5 |  |  | 0.62537 | 0 | 0.62537 | Grid Faults
2023-11-12 |  |  | 1 | 6 |  |  | 0.74492 | 0 | 0.74492 | Grid Faults
2023-11-13 |  |  | 1 | 12 |  |  | 1.4724 | 0 | 1.4724 | Grid Faults
2023-11-14 | [6 empty] | 0 | 0 | 0 | Grid Faults
2023-11-15 | [6 empty] | 0 | 0 | 0
2023-11-16 | [6 empty] | 0 | 0 | 0
2023-11-17 |  |  | 1 | 6 |  |  | 0.68269 | 0 | 0.68269
2023-11-18 | [6 empty] | 0 | 0 | 0
2023-11-19 |  |  | 1 | 5 |  |  | 0.5524 | 0 | 0.5524
2023-11-20 | [6 empty] | 0 | 0 | 0
2023-11-21 |  |  | 1 | 14 |  |  | 1.5065 | 0 | 1.5065
2023-11-22 | [6 empty] | 0 | 0 | 0
2023-11-23 | [6 empty] | 0 | 0 | 0
2023-11-24 | [6 empty] | 0 | 0 | 0
2023-11-25 | [6 empty] | 0 | 0 | 0
2023-11-26 | [6 empty] | 0 | 0 | 0
2023-11-27 | [6 empty] | 0 | 0 | 0
2023-11-28 | [6 empty] | 0 | 0 | 0 | Unit I stopped for higher efficiency
2023-11-29 |  |  | 2 | 33 |  |  | 3.2181 | 0 | 3.2181 | shutdown for transmission tree cutting
2023-11-30 |  |  | 1 | 7 |  |  | 0.67622 | 0 | 0.67622
2023-12-01 | [6 empty] | 0 | 0 | 0
2023-12-02 |  |  | 1 | 7 |  |  | 0.64582 | 0 | 0.64582
2023-12-03 | [6 empty] | 0 | 0 | 0 | Unit I stopped as plant was running at 5.2 MW in the morning
2023-12-04 | [6 empty] | 0 | 0 | 0
2023-12-05 |  |  | 2 | 47 |  |  | 4.3376 | 0 | 4.3376 | Shutdown for tree cutting
2023-12-06 |  |  | 1 | 43 |  |  | 3.8682 | 0 | 3.8682
2023-12-07 |  |  | 2 | 36 |  |  | 3.292 | 0 | 3.292 | Shutdown for replacing 100 kVA transformer
2023-12-08 | [6 empty] | 0 | 0 | 0
2023-12-09 | [6 empty] | 0 | 0 | 0
2023-12-10 |  |  | 1 | 6 |  |  | 0.5192 | 0 | 0.5192
2023-12-11 | [6 empty] | 0 | 0 | 0
2023-12-12 | [6 empty] | 0 | 0 | 0
2023-12-13 |  |  | 4 | 39 |  |  | 3.3026 | 0 | 3.3026
2023-12-14 | [6 empty] | 0 | 0 | 0
2023-12-15 |  |  | 1 | 82 |  |  | 6.8809 | 0 | 6.8809
2023-12-16 |  |  | 2 | 16 |  |  | 1.3087 | 0 | 1.3087
2023-12-17 |  |  | 1 | 14 |  |  | 1.1227 | 0 | 1.1227
2023-12-18 | [6 empty] | 0 | 0 | 0
2023-12-19 |  |  | 1 | 12 |  |  | 0.91745 | 0 | 0.91745 | Testing works for Circuit breaker closing for synchronization.
2023-12-20 |  |  | 3 | 25 |  |  | 1.9507 | 0 | 1.9507 | Testing works for Circuit breaker closing for synchronization.
2023-12-21 |  |  | 1 | 69 |  |  | 5.5169 | 0 | 5.5169 | Exchange of circuit breaker from Unit I to Unit II
2023-12-22 |  |  | 3 | 41 |  |  | 3.2256 | 0 | 3.2256 | Testing works for Circuit breaker closing for synchronization and Grid Faults
2023-12-23 |  |  | 1 | 11 |  |  | 0.84797 | 0 | 0.84797 | Testing works for Faults clearance for both units
2023-12-24 |  |  | 4 | 71 |  |  | 5.5699 | 0 | 5.5699
2023-12-25 |  |  | 1 | 9 |  |  | 0.67569 | 0 | 0.67569
2023-12-26 |  |  | 1 | 7 |  |  | 0.52512 | 0 | 0.52512
2023-12-27 | [6 empty] | 0 | 0 | 0
2023-12-28 | [6 empty] | 0 | 0 | 0
2023-12-29 |  |  | 1 | 7 |  |  | 0.50339 | 0 | 0.50339
2023-12-30 | [6 empty] | 0 | 0 | 0
2023-12-31 | [6 empty] | 0 | 0 | 0
2024-01-01 | [6 empty] | 0 | 0 | 0
2024-01-02 | [6 empty] | 0 | 0 | 0
2024-01-03 | [6 empty] | 0 | 0 | 0
2024-01-04 |  |  | 2 | 46 |  |  | 3.1023 | 0 | 3.1023 | Shutdown for tree cutting
2024-01-05 | [6 empty] | 0 | 0 | 0
2024-01-06 |  |  | 1 | 31 |  |  | 2.0955 | 0 | 2.0955 | Shutdown for tree cutting
2024-01-07 | [6 empty] | 0 | 0 | 0
2024-01-08 |  |  | 2 | 36 |  |  | 2.3783 | 0 | 2.3783 | Shutdown for tree cutting
2024-01-09 |  |  | 2 | 63 |  |  | 4.1446 | 0 | 4.1446 | Shutdown for tree cutting
2024-01-10 | [6 empty] | 0 | 0 | 0
2024-01-11 | [6 empty] | 0 | 0 | 0
2024-01-12 | [6 empty] | 0 | 0 | 0
2024-01-13 | [6 empty] | 0 | 0 | 0
2024-01-14 | [6 empty] | 0 | 0 | 0
2024-01-15 | [6 empty] | 0 | 0 | 0
2024-01-16 | [6 empty] | 0 | 0 | 0
2024-01-17 | [6 empty] | 0 | 0 | 0
2024-01-18 |  |  | 2 | 84 |  |  | 5.231 | 0 | 5.231 | Grid Faults
2024-01-19 |  |  | 1 | 33 |  |  | 2.0032 | 0 | 2.0032 | Grid Faults
2024-01-20 | [6 empty] | 0 | 0 | 0
2024-01-21 | [6 empty] | 0 | 0 | 0
2024-01-22 | [6 empty] | 0 | 0 | 0
2024-01-23 | [6 empty] | 0 | 0 | 0
2024-01-24 | [6 empty] | 0 | 0 | 0
2024-01-25 |  |  |  |  | 1 | 32 | 0 | 2.75 | 2.75
2024-01-26 | [6 empty] | 0 | 0 | 0
2024-01-27 | [6 empty] | 0 | 0 | 0
2024-01-28 | [6 empty] | 0 | 0 | 0
2024-01-29 | [6 empty] | 0 | 0 | 0
2024-01-30 | [6 empty] | 0 | 0 | 0
2024-01-31 | [6 empty] | 0 | 0 | 0
2024-02-01 | [6 empty] | 0 | 0 | 0
2024-02-02 | [6 empty] | 0 | 0 | 0
2024-02-03 |  |  | 1 | 3 |  |  | 0.16502 | 0 | 0.16502
2024-02-04 | [6 empty] | 0 | 0 | 0
2024-02-05 | [6 empty] | 0 | 0 | 0
2024-02-06 | [6 empty] | 0 | 0 | 0
2024-02-07 |  |  | 1 | 6 |  |  | 0.31914 | 0 | 0.31914
2024-02-08 | [6 empty] | 0 | 0 | 0
2024-02-09 | [6 empty] | 0 | 0 | 0
2024-02-10 | [6 empty] | 0 | 0 | 0
2024-02-11 | [6 empty] | 0 | 0 | 0
2024-02-12 |  |  | 2 | 22 |  |  | 1.1714 | 0 | 1.1714
2024-02-13 | [6 empty] | 0 | 0 | 0
2024-02-14 | [6 empty] | 0 | 0 | 0
2024-02-15 | [6 empty] | 0 | 0 | 0
2024-02-16 |  |  | 1 | 6 |  |  | 0.31112 | 0 | 0.31112
2024-02-17 | [6 empty] | 0 | 0 | 0
2024-02-18 | [6 empty] | 0 | 0 | 0
2024-02-19 | [6 empty] | 0 | 0 | 0
2024-02-20 | [6 empty] | 0 | 0 | 0
2024-02-21 |  |  | 1 | 14 |  |  | 0.75953 | 0 | 0.75953
2024-02-22 | [6 empty] | 0 | 0 | 0
2024-02-23 | [6 empty] | 0 | 0 | 0
2024-02-24 | [6 empty] | 0 | 0 | 0
2024-02-25 | [6 empty] | 0 | 0 | 0
2024-02-26 | [6 empty] | 0 | 0 | 0
2024-02-27 | [6 empty] | 0 | 0 | 0
2024-02-28 | [6 empty] | 0 | 0 | 0
2024-02-29 | [6 empty] | 0 | 0 | 0
2024-03-01 | [6 empty] | 0 | 0 | 0
2024-03-02 | [6 empty] | 0 | 0 | 0
2024-03-03 | [6 empty] | 0 | 0 | 0
2024-03-04 |  |  | 5 | 106 |  |  | 6.3349 | 0 | 6.3349
2024-03-05 | [6 empty] | 0 | 0 | 0
2024-03-06 | [6 empty] | 0 | 0 | 0
2024-03-07 | [6 empty] | 0 | 0 | 0
2024-03-08 | [6 empty] | 0 | 0 | 0
2024-03-09 | [6 empty] | 0 | 0 | 0
2024-03-10 |  |  | 2 | 11 |  |  | 0.66639 | 0 | 0.66639
2024-03-11 | [6 empty] | 0 | 0 | 0
2024-03-12 | [6 empty] | 0 | 0 | 0
2024-03-13 | [6 empty] | 0 | 0 | 0
2024-03-14
2024-03-15 | [6 empty] | 0 | 0 | 0
2024-03-16 | [6 empty] | 0 | 0 | 0
2024-03-17 | [6 empty] | 0 | 0 | 0
2024-03-18 |  |  | 1 | 34 |  |  | 1.9915 | 0 | 1.9915 | Due to trip in Balanch ground current
2024-03-19 | [6 empty] | 0 | 0 | 0
2024-03-20 | [6 empty] | 0 | 0 | 0
2024-03-21 | [6 empty] | 0 | 0 | 0
2024-03-22 | [6 empty] | 0 | 0 | 0
2024-03-23 |  |  | 1 | 847 |  |  | 46.6956 | 0 | 46.6956 | Jumper out in triple pole at nalabagad
2024-03-24 | [6 empty] | 0 | 0 | 0
2024-03-25 | [6 empty] | 0 | 0 | 0
2024-03-26 | [6 empty] | 0 | 0 | 0
2024-03-27 | [6 empty] | 0 | 0 | 0
2024-03-28 | [6 empty] | 0 | 0 | 0
2024-03-29 | [6 empty] | 0 | 0 | 0
2024-03-30 | [6 empty] | 0 | 0 | 0
2024-03-31 |  |  | 1 | 5 |  |  | 0.45154 | 0 | 0.45154 | Grid faults
2024-04-01 | [6 empty] | 0 | 0 | 0
2024-04-02 |  |  | 1 | 58 |  |  | 4.6196 | 0 | 4.6196 | Installation of dampers in pole no. 111 at nalabagad
2024-04-03 | [6 empty] | 0 | 0 | 0
2024-04-04 |  |  | 2 | 51 |  |  | 4.9459 | 0 | 4.9459 | Grid faults
2024-04-05 |  |  | 1 | 5 |  |  | 0.43541 | 0 | 0.43541 | Grid faults
2024-04-06 | [6 empty] | 0 | 0 | 0
2024-04-07 |  |  | 1 | 6 |  |  | 0.53014 | 0 | 0.53014 | Grid faults
2024-04-08 | [6 empty] | 0 | 0 | 0
2024-04-09 | [6 empty] | 0 | 0 | 0
2024-04-10 |  |  | 1 | 11 |  |  | 0.86495 | 0 | 0.86495 | Grid faults
2024-04-11 | [6 empty] | 0 | 0 | 0
2024-04-12 | [6 empty] | 0 | 0 | 0
2024-04-13 | [6 empty] | 0 | 0 | 0
2024-04-14 |  |  | 1 | 6 |  |  | 0.53061 | 0 | 0.53061
2024-04-15 | [6 empty] | 0 | 0 | 0
2024-04-16 |  |  | 2 | 41 |  |  | 3.8411 | 0 | 3.8411 | Grid faults and DDLO issue
2024-04-17 | [6 empty] | 0 | 0 | 0
2024-04-18 |  |  | 1 | 13 |  |  | 1.8327 | 0 | 1.8327 | Issue in our system
2024-04-19 | [6 empty] | 0 | 0 | 0 | Unit 2 tripped due to hydraulic pipe damage
2024-04-20 | [6 empty] | 0 | 0 | 0
2024-04-21 | [6 empty] | 0 | 0 | 0
2024-04-22 |  |  | 1 | 5 |  |  | 0.70634 | 0 | 0.70634 | Grid faults
2024-04-23 | [6 empty] | 0 | 0 | 0
2024-04-24 | [6 empty] | 0 | 0 | 0
2024-04-25 |  |  | 1 | 200 |  |  | 20.9619 | 0 | 20.9619 | Penstock repair work at AB3 location
2024-04-26 |  |  | 1 | 1440 |  |  |  | 150.93 | 150.93 | Penstock repair work at AB3 location
2024-04-27 |  |  | 1 |  | 336 | 336 | 0 | 56 | 56 | Penstock repair work at AB3 location
2024-04-28 |  |  | 1 | 6 |  |  | 0.58391 | 0 | 0.58391 | Grid faults
2024-04-29 | [6 empty] | 0 | 0 | 0
2024-04-30 |  |  | 2 | 13 | 23 | 23 | 1.3712 | 3.8333 | 5.2045 | DDLO issue and Grid faults
2024-05-01 | [6 empty] | 0 | 0 | 0
2024-05-02 | [6 empty] | 0 | 0 | 0
2024-05-03 | [6 empty] | 0 | 0 | 0
2024-05-04 | [6 empty] | 0 | 0 | 0
2024-05-05 | [6 empty] | 0 | 0 | 0
2024-05-06 |  |  | 1 | 25 |  |  | 2.2321 | 0 | 2.2321 | Grid faults
2024-05-07 |  |  | 1 |  | 8 | 8 | 0 | 1.3333 | 1.3333 | Optical cable damage
2024-05-08 |  |  | 1 |  | 7 | 7 | 0 | 1.1667 | 1.1667 | Optical cable issue
2024-05-09 |  |  | 1 | 8 |  |  | 0.6563 | 0 | 0.6563 | Grid faults
2024-05-10 | [6 empty] | 0 | 0 | 0
2024-05-11 |  |  | 3 | 61 |  |  | 5.7859 | 0 | 5.7859 | Grid faults
2024-05-12 |  |  | 1 | 5 |  |  | 0.48786 | 0 | 0.48786 | Grid faults
2024-05-13 | [6 empty] | 0 | 0 | 0
2024-05-14 |  |  | 1 | 5 |  |  | 0.60566 | 0 | 0.60566 | Grid faults
2024-05-15 |  |  | 4 | 36 |  |  | 3.9406 | 0 | 3.9406 | Grid Faults
2024-05-16 |  |  | 1 |  | 6 | 6 | 0 | 1 | 1 | Test for penstok shaking
2024-05-17 | [6 empty] | 0 | 0 | 0
2024-05-18 | [6 empty] | 0 | 0 | 0
2024-05-19 |  |  | 2 | 37 |  |  | 3.4531 | 0 | 3.4531 | Grid Faults
2024-05-20 | [6 empty] | 0 | 0 | 0
2024-05-21 |  |  | 4 | 29 |  |  | 3.2164 | 0 | 3.2164 | Grid Faults
2024-05-22 |  |  | 3 | 13 |  |  | 1.4316 | 0 | 1.4316 | Grid Faults
2024-05-23 | [6 empty] | 0 | 0 | 0
2024-05-24 | [6 empty] | 0 | 0 | 0
2024-05-25 | [6 empty] | 0 | 0 | 0
2024-05-26 | [6 empty] | 0 | 0 | 0
2024-05-27 |  |  | 2 | 10 |  |  | 1.0214 | 0 | 1.0214 | Grid Faults
2024-05-28 | [6 empty] | 0 | 0 | 0
2024-05-29 |  |  | 1 | 7 |  |  | 0.956 | 0 | 0.956 | Grid Faults
2024-05-30 |  |  | 3 |  | 40 | 40 | 0 | 6.6667 | 6.6667 | DDLO issue and wind
2024-05-31 |  |  | 3 | 15 | 63 | 63 | 1.6189 | 10.5 | 12.1189 | DDLO repair, water level and grid fault
2024-06-01 | [6 empty] | 0 | 0 | 0
2024-06-02 |  |  | 1 | 10 |  |  | 0.87012 | 0 | 0.87012 | Grid Faults
2024-06-03 |  |  | 1 | 50 |  |  | 4.2961 | 0 | 4.2961 | Grid Faults
2024-06-04 |  |  | 2 | 15 |  |  | 1.2602 | 0 | 1.2602 | Grid Faults
2024-06-05 |  |  | 3 | 20 |  |  | 1.6793 | 0 | 1.6793 | Grid Faults
2024-06-06 | 87.08 | 1046 | 1 |  |  |  | 0 | 0 | 0 | 132 kV line after Syaule hit by tree
2024-06-07 | 17.76 | 210 | 3 | 50 |  |  | 4.2286 | 0 | 4.2286 | Grid Faults
2024-06-08 | 0 | [5 empty] | 0 | 0 | 0
2024-06-09 | 0 | [5 empty] | 0 | 0 | 0
2024-06-10 | 0 |  | 1 | 2 |  |  | 0.14573 | 0 | 0.14573 | Grid Faults
2024-06-11 | 0 | [5 empty] | 0 | 0 | 0
2024-06-12 | 0 |  | 2 | 9 |  |  | 0.62361 | 0 | 0.62361 | Grid Faults
2024-06-13 | 0 | [5 empty] | 0 | 0 | 0
2024-06-14 | 0 |  | 3 | 36 |  |  | 2.4281 | 0 | 2.4281 | Grid Faults
2024-06-15 | 0 |  | 2 | 9 |  |  | 0.63016 | 0 | 0.63016 | Grid Faults
2024-06-16 |  |  | 1 | 4 |  |  | 0.26102 | 0 | 0.26102 | Grid Faults
2024-06-17 | [6 empty] | 0 | 0 | 0
2024-06-18 |  |  | 1 | 52 |  |  | 3.9488 | 0 | 3.9488 | Grid Faults
2024-06-19 | [6 empty] | 0 | 0 | 0
2024-06-20 |  |  | 4 | 74 |  |  | 9.1644 | 0 | 9.1644 | Grid Faults
2024-06-21 |  |  | 1 | 63 |  |  | 6.0437 | 0 | 6.0437 | Grid Faults
2024-06-22 | [6 empty] | 0 | 0 | 0
2024-06-23 | [6 empty] | 0 | 0 | 0
2024-06-24 | [6 empty] | 0 | 0 | 0
2024-06-25 |  |  | 1 | 4 |  |  | 0.40669 | 0 | 0.40669 | Grid Faults
2024-06-26 |  |  | 1 | 42 |  |  | 4.2735 | 0 | 4.2735 | Grid Faults
2024-06-27 | [6 empty] | 0 | 0 | 0
2024-06-28 |  |  | 3 | 23 |  |  | 3.8919 | 0 | 3.8919 | Grid Faults
2024-06-29 | [6 empty] | 0 | 0 | 0
2024-06-30 |  |  | 2 | 10 |  |  | 1.7303 | 0 | 1.7303 | Grid Faults
2024-07-01 |  |  | 2 | 8 |  |  | 1.389 | 0 | 1.389 | Grid Faults
2024-07-02 |  |  | 1 | 5 |  |  | 0.86451 | 0 | 0.86451 | Grid Faults
2024-07-03 |  |  | 6 | 35 |  |  | 6.0386 | 0 | 6.0386 | Grid Faults
2024-07-04 |  |  | 3 | 14 |  |  | 2.3844 | 0 | 2.3844 | Grid Faults
2024-07-05 |  |  | 1 | 108 |  |  | 18.0908 | 0 | 18.0908 | Spear Valve and optical cable damage
2024-07-06 | [6 empty] | 0 | 0 | 0
2024-07-07 |  |  | 4 | 447 |  |  | 72.7689 | 0 | 72.7689 | Intake trashrack covered by debris, Grid faults
2024-07-08 |  |  | 1 | 1164 |  |  | 193.2634 | 0 | 193.2634 | Penstock pipe expansion joint leakage/ spear valve issue
2024-07-09 |  |  | 1 | 1164 |  |  | 194 | 0 | 194 | Penstock pipe expansion joint leakage repair
2024-07-10 |  |  | 1 | 1164 |  |  | 194 | 0 | 194 | Penstock pipe expansion joint leakage repair
2024-07-11 |  |  | 1 | 534 |  |  | 91.8717 | 0 | 91.8717 | Penstock pipe expansion joint leakage repair
2024-07-12 | [6 empty] | 0 | 0 | 0
2024-07-13 |  |  | 1 | 1020 |  |  | 175.108 | 0 | 175.108 | Transmission line issue at Balanch
2024-07-14 |  |  | 1 | 385 |  |  | 65.3702 | 0 | 65.3702 | Transmission line issue at Balanch
2024-07-15 |  |  | 3 | 13 |  |  | 2.2553 | 0 | 2.2553 | Grid Faults
2024-07-16 | [6 empty] | 0 | 0 | 0
2024-07-17 | [6 empty] | 0 | 0 | 0
2024-07-18 |  |  | 1 | 8 |  |  | 1.3966 | 0 | 1.3966 | Grid Faults
2024-07-19 | [6 empty] | 0 | 0 | 0
2024-07-20 |  |  | 2 | 19 | 248 |  | 3.2814 | 20.6667 | 23.9481 | Grid Faults + Unit I spear valve repair
2024-07-21 |  |  | 1 |  | 570 | 270 | 0 | 70 | 70 | Unit I and Unit II spear valve repair
2024-07-22 |  |  | 1 |  | 10 | 348 | 0 | 29.8333 | 29.8333 | Unit II spear valve repair + Unit I spear valve feedback setting
2024-07-23 | [6 empty] | 0 | 0 | 0
2024-07-24 | [6 empty] | 0 | 0 | 0
2024-07-25 | [6 empty] | 0 | 0 | 0
2024-07-26 | [6 empty] | 0 | 0 | 0
2024-07-27 |  |  | 2 | 18 |  |  | 3.1392 | 0 | 3.1392 | Grid Faults
2024-07-28 |  |  | 1 |  | 1038 | 1050 | 0 | 174 | 174 | Double pole at powerhouse in a risky situation
2024-07-29 |  |  | 1 |  | 282 | 282 | 0 | 47 | 47 | Double pole at powerhouse in a risky situation
2024-07-30 |  |  | 1 |  |  | 7 | 0 | 0.58333 | 0.58333 | Pressure increased upto 160 bar in MIV Oil unit
2024-07-31 |  |  | 3 | 14 | 100 | 100 | 2.4389 | 16.6667 | 19.1056 | Grid Faults and DDLO repair
2024-08-01 | 7.847 | 45.044 | 1 | 6 |  |  | 1.0125 | 0 | 1.0125 | Grid Faults and Dispatch instruction by LDC to reduce power to 9 MW
2024-08-02 |  | 0 |  |  |  |  | 0 | 0 | 0
2024-08-03 |  | 0 | 3 | 27 |  |  | 4.7197 | 0 | 4.7197 | Grid Faults
2024-08-04 | 12.7196 | 72.765 |  |  |  |  | 0 | 0 | 0 | Dispatch instruction from LDC to run the plant at 6 MW
2024-08-05 | 10.8481 | 65.3613 | 5 | 192 |  |  | 32.1536 | 0 | 32.1536 | Dispatch instruction from LDC to run the plant at 6 MW / Grid fault / Forced outage
2024-08-06 | [6 empty] | 0 | 0 | 0
2024-08-07 | 26.2176 | 151.0144 | 1 | 5 |  |  | 0.78397 | 0 | 0.78397 | Dispatch instruction from LDC to run the plant at 6 MW / Grid fault
2024-08-08 | 1.5215 | 9.7037 | 2 | 11 | 60 | 50 | 1.9134 | 9.1667 | 11.08 | Grid Faults/ blockage in trashrack
2024-08-09 | 3.2746 | 18.8257 | 1 | 120 |  |  | 20.7271 | 0 | 20.7271 | Emergency shutdown due to risk of landslide, backside of powerhouse / LDC dispatch to run plant at 8 MW
2024-08-10 | 3.0017 | 17.3786 |  |  |  |  | 0 | 0 | 0 | LDC dispatch to run plant at 9 MW
2024-08-11 | 6.0017 | 34.7089 |  |  |  |  | 0 | 0 | 0 | LDC dispatch to run plant at 9 MW / 8 MW
2024-08-12 | 6.0017 | 35.1322 |  |  |  |  | 0 | 0 | 0 | LDC dispatch to run plant at 9 MW
2024-08-13 | [6 empty] | 0 | 0 | 0
2024-08-14 |  |  | 1 | 5 |  |  | 0.86062 | 0 | 0.86062 | Grid Faults
2024-08-15 | [6 empty] | 0 | 0 | 0
2024-08-16 | [6 empty] | 0 | 0 | 0
2024-08-17 | 0.00175 | 0.01 |  |  |  |  | 0 | 0 | 0 | LDC dispatch to run plant at 8 MW
2024-08-18 | -1.7313e-05 | -9.8929e-05 | 1 | 3 |  |  | 0.52192 | 0 | 0.52192 | Grid Faults
2024-08-19 | 0 | 0 |  |  |  |  | 0 | 0 | 0
2024-08-20 | 0 | 0 | 1 | 16 |  |  | 2.7865 | 0 | 2.7865 | Grid Faults
2024-08-21 | 7.7622 | 44.0882 |  |  |  |  | 0 | 0 | 0 | LDC dispatch instruction
2024-08-22 | 8.7622 | 49.7681 |  |  |  |  | 0 | 0 | 0 | LDC dispatch instruction
2024-08-23 |  | 0 |  |  |  |  | 0 | 0 | 0
2024-08-24 | 0 | 0 | 1 | 10 |  |  | 1.7622 | 0 | 1.7622 | Grid Faults
2024-08-25 |  | 0 | 2 | 16 |  |  | 2.809 | 0 | 2.809 | Grid Faults
2024-08-26 |  | 0 | 1 | 9 |  |  | 1.5723 | 0 | 1.5723 | Grid Faults
2024-08-27 | 14.5995 | 82.9236 | 1 | 7 |  |  | 1.1626 | 0 | 1.1626 | LDC dispatch instruction + Grid Faults
2024-08-28 | 5.7622 | 32.7285 |  |  |  |  | 0 | 0 | 0 | LDC dispatch instruction
2024-08-29 |  |  | 2 | 12 |  |  | 2.1092 | 0 | 2.1092 | Grid Faults
2024-08-30 |  |  | 2 | 21 |  |  | 3.6554 | 0 | 3.6554 | Grid Faults
2024-08-31 | 6.7034 | 38.0743 | 2 | 12 |  |  | 2.0588 | 0 | 2.0588 | LDC dispatch instruction + Grid Faults
2024-09-01 |  |  | 1 | 3 |  |  | 0.52609 | 0 | 0.52609 | Grid Faults
2024-09-02 |  |  | 1 | 4 |  |  | 0.69916 | 0 | 0.69916 | Grid Faults
2024-09-03 |  |  | 1 | 6 |  |  | 1.0502 | 0 | 1.0502 | Grid Faults
2024-09-04 |  |  | 1 | 6 |  |  | 1.046 | 0 | 1.046 | Grid Faults + Unit 2 delay for taking data of MIV
2024-09-05 |  |  | 2 | 12 |  |  | 2.1008 | 0 | 2.1008 | Grid Faults
2024-09-06 |  |  | 1 | 3 |  |  | 0.52609 | 0 | 0.52609 | Grid Faults
2024-09-07 | 6.5605 | 37.2629 | 2 | 7 |  |  | 1.2017 | 0 | 1.2017 | LDC dispatch instruction + Grid Faults
2024-09-08 |  |  | 1 |  | 35 | 35 | 0 | 5.8333 | 5.8333 | Tree and Bush cutting at Latinath
2024-09-09 |  |  | 1 | 3 |  |  | 0.52609 | 0 | 0.52609 | Grid Faults
2024-09-10 | [6 empty] | 0 | 0 | 0
2024-09-11 | 4.6483 |  | 2 | 18 |  |  | 3.1139 | 0 | 3.1139 | LDC dispatch instruction + Grid Faults
2024-09-12 |  |  | 9 | 59 |  |  | 10.2961 | 0 | 10.2961 | Grid Faults
2024-09-13 |  |  | 10 | 163 |  |  | 28.3365 | 0 | 28.3365 | Grid Faults
2024-09-14 |  |  | 2 | 6 |  |  | 1.0502 | 0 | 1.0502 | Grid Faults
2024-09-15 | 41.493 | 235.6754 | 3 | 24 |  |  | 3.5084 | 0 | 3.5084 | LDC dispatch instruction + Grid Faults
2024-09-16 | 42.0015 | 238.5633 |  |  |  |  | 0 | 0 | 0 | LDC dispatch instruction
2024-09-17 | 39.0015 | 221.5238 |  |  |  |  | 0 | 0 | 0 | LDC dispatch instruction
2024-09-18 | 26.2176 | 149.8149 | 1 | 5 |  |  | 0.78397 | 0 | 0.78397 | Dispatch Instruction + Grid Faults
2024-09-19 | 35.0015 | 200.0086 |  |  |  |  | 0 | 0 | 0 | Dispatch Instruction
2024-09-20 | 21.0016 | 120.0092 |  |  |  |  | 0 | 0 | 0 | Dispatch Instruction
2024-09-21 | 3.0017 | 17.1527 |  |  |  |  | 0 | 0 | 0 | Dispatch Instruction
2024-09-22 |  |  | 3 | 46 |  |  | 8.0516 | 0 | 8.0516 | Grid Faults
2024-09-23 |  |  | 1 | 168 |  |  | 29.3205 | 0 | 29.3205 | Grid Faults (Issue in busbar at Balanch)
2024-09-24 | 1.567 | 8.9541 | 1 |  |  | 5 | 0 | 0.41667 | 0.41667 | Dispatch Instruction +Unit II shutdown
2024-09-25 |  |  | 1 | 80 |  |  | 13.9999 | 0 | 13.9999 | Grid Faults (Issue in 132 kV tx line one circuit from Balanch to Attariya)
2024-09-26 | 69.6213 | 397.8361 | 1 | 3 |  |  | 0.37996 | 0 | 0.37996 | Dispatch Instruction + Grid Faults
2024-09-27 | 52.1688 | 298.1072 | 1 | 6 |  |  | 0.83263 | 0 | 0.83263 | Dispatch Instruction + Grid Faults
2024-09-28 | 46.5777 | 266.1584 | 1 | 24 |  |  | 3.4237 | 0 | 3.4237 | Dispatch Instruction + Grid Faults
2024-09-29 | 45.0014 | 257.1511 |  |  |  |  | 0 | 0 | 0 | Dispatch Instruction
2024-09-30 | 56.9176 | 325.2432 | 1 | 8 |  |  | 1.0838 | 0 | 1.0838 | Dispatch Instruction + Grid Faults
2024-10-01 | 43.186 | 246.7771 | 2 | 47 |  |  | 6.8155 | 0 | 6.8155 | Dispatch Instruction + Grid Faults
2024-10-02 | 18.7055 | 106.8888 | 2 | 8 |  |  | 1.2961 | 0 | 1.2961 | Dispatch Instruction + Grid Faults
2024-10-03 |  |  | 1 | 5 |  |  | 0.87804 | 0 | 0.87804 | Grid Faults
2024-10-04 | 1.567 | 8.9541 | 3 | 14 |  |  | 2.4348 | 0 | 2.4348 | Dispatch Instruction + Grid Faults
2024-10-05 | 2.0017 | 11.4385 |  |  |  |  | 0 | 0 | 0 | Dispatch Instruction
2024-10-06 | 7.0017 | 40.0097 |  |  |  |  | 0 | 0 | 0 | Dispatch Instruction
2024-10-07 | [6 empty] | 0 | 0 | 0
2024-10-08 | [6 empty] | 0 | 0 | 0
2024-10-09 | 5.0017 | 28.5812 |  |  |  |  | 0 | 0 | 0 | Dispatch Instruction
2024-10-10 | 15.0016 | 85.7237 |  |  |  |  | 0 | 0 | 0 | Dispatch Instruction
2024-10-11 | [6 empty] | 0 | 0 | 0
2024-10-12 | 11.0017 | 62.8667 |  |  |  |  | 0 | 0 | 0 | Dispatch Instruction
2024-10-13 | 2.1341 | 12.1951 | 1 | 5 |  |  | 0.86759 | 0 | 0.86759 | Dispatch Instruction + Grid Faults
2024-10-14 | 3.0017 | 17.1527 |  |  |  |  | 0 | 0 | 0 | Dispatch Instruction
2024-10-15 | 0.00175 | 0.0099999 |  |  |  |  | 0 | 0 | 0 | Dispatch Instruction
2024-10-16 | 0.00175 | 0.0099999 |  |  |  |  | 0 | 0 | 0 | Dispatch Instruction
2024-10-17 | 2.0017 | 11.4385 |  |  |  |  | 0 | 0 | 0 | Dispatch Instruction
2024-10-18 | 0.00175 | 0.0099999 |  |  |  |  | 0 | 0 | 0
2024-10-19 | 0.00175 | 0.0099999 |  |  |  |  | 0 | 0 | 0
2024-10-20 | [6 empty] | 0 | 0 | 0
2024-10-21 | 8.3248 | 47.5704 | 1 | 4 |  |  | 0.67688 | 0 | 0.67688 | Grid Faults + LDC Dispatch instruction to 7 MW
2024-10-22 | [6 empty] | 0 | 0 | 0
2024-10-23 | [6 empty] | 0 | 0 | 0
2024-10-24 | [6 empty] | 0 | 0 | 0
2024-10-25 | [6 empty] | 0 | 0 | 0
2024-10-26 | 3.1376 | 17.9293 | 1 | 5 |  |  | 0.86411 | 0 | 0.86411 | Grid Faults + LDC Dispatch instruction to 9 MW
2024-10-27 | [6 empty] | 0 | 0 | 0
2024-10-28 | [6 empty] | 0 | 0 | 0
2024-10-29 | [6 empty] | 0 | 0 | 0
2024-10-30 | [6 empty] | 0 | 0 | 0
2024-10-31 | 0.20163 | 1.1522 |  |  |  |  | 0 | 0 | 0 | LDC Dispatch instruction to 8.5 MW
2024-11-01 | [6 empty] | 0 | 0 | 0
2024-11-02 | [6 empty] | 0 | 0 | 0
2024-11-03 | [6 empty] | 0 | 0 | 0 | LDC Dispatch instruction to 5 MW
2024-11-04 | [6 empty] | 0 | 0 | 0
2024-11-05 | [6 empty] | 0 | 0 | 0
2024-11-06 | [6 empty] | 0 | 0 | 0
2024-11-07 | [6 empty] | 0 | 0 | 0
2024-11-08 |  |  | 2 |  | 14 | 4 | 0 | 1.5 | 1.5 | Automation works
2024-11-09 |  |  | 1 | 5 |  |  | 0.69686 | 0 | 0.69686 | Grid Faults
2024-11-10 |  |  | 1 |  | 230 | 220 | 0 | 37.5 | 37.5 | Automation works + Station Transformer Panel Install
2024-11-11 |  |  | 2 |  | 360 | 360 | 0 | 60 | 60 | Automation works + Station Transformer Panel Install
2024-11-12 |  |  | 3 | 62 |  |  | 8.5036 | 0 | 8.5036 | Install smart meter in Balanch, Automation works
2024-11-13 |  |  | 6 |  | 88 | 65 | 0 | 12.75 | 12.75 | Automation works
2024-11-14 |  |  | 2 | 5 | 60 | 60 | 0.65454 | 7.8 | 8.4545 | Grid Faults + Automation works
2024-11-15 | [6 empty] | 0 | 0 | 0
2024-11-16 |  |  | 1 |  | 180 | 180 | 0 | 23.4 | 23.4 | Automation works
2024-11-17 |  |  | 1 | 15 | 81 | 112 | 1.8517 | 12.545 | 14.3967 | Automation Works + Grid Failure
2024-11-18 |  |  | 1 |  | 138 | 138 | 0 | 17.94 | 17.94 | Automation Works
2024-11-19 |  |  | 8 |  | 112 | 215 | 0 | 21.255 | 21.255 | Automation Works + MV Panel H04 repair
2024-11-20 |  |  | 20 |  | 114 | 79 | 0 | 12.545 | 12.545 | Automation Works
2024-11-21 |  |  | 3 |  | 88 | 0 | 0 | 5.72 | 5.72 | Automation Works
2024-11-22 |  |  | 2 |  |  | 19 | 0 | 1.1601 | 1.1601 | Automation Works
2024-11-23 |  |  | 1 |  | 12 | 12 | 0 | 1.5013 | 1.5013 | Automation Works
2024-11-24 | [6 empty] | 0 | 0 | 0
2024-11-25 | [6 empty] | 0 | 0 | 0
2024-11-26 | [6 empty] | 0 | 0 | 0
2024-11-27 | [6 empty] | 0 | 0 | 0
2024-11-28 | [6 empty] | 0 | 0 | 0
2024-11-29 | [6 empty] | 0 | 0 | 0
2024-11-30 | [6 empty] | 0 | 0 | 0
2024-12-01 |  |  | 1 | 4 |  |  | 0.4039 | 0 | 0.4039 | Grid Faults
2024-12-02 | [6 empty] | 0 | 0 | 0
2024-12-03 | [6 empty] | 0 | 0 | 0
2024-12-04 | [6 empty] | 0 | 0 | 0
2024-12-05 | [6 empty] | 0 | 0 | 0
2024-12-06 | [6 empty] | 0 | 0 | 0
2024-12-07 |  |  | 2 |  | 1 | 1 | 0 | 0.112 | 0.112 | Operator Training
2024-12-08 | [6 empty] | 0 | 0 | 0
2024-12-09 | [6 empty] | 0 | 0 | 0
2024-12-10 |  |  | 2 |  | 12 | 12 | 0 | 1.319 | 1.319 | Power Issue for water level sensor
2024-12-11 | [6 empty] | 0 | 0 | 0
2024-12-12 | [6 empty] | 0 | 0 | 0
2024-12-13 | [6 empty] | 0 | 0 | 0
2024-12-14 | [6 empty] | 0 | 0 | 0
2024-12-15 |  |  | 1 | 4 |  |  | 0.34262 | 0 | 0.34262 | Grid Faults
2024-12-16 | [6 empty] | 0 | 0 | 0
2024-12-17 | [6 empty] | 0 | 0 | 0
2024-12-18 | [6 empty] | 0 | 0 | 0
2024-12-19 | [6 empty] | 0 | 0 | 0
2024-12-20 | [6 empty] | 0 | 0 | 0
2024-12-21 |  |  | 1 |  | 20 |  | 0 | 1.3 | 1.3 | Shutdown for cable stinging in insulator
2024-12-22 |  |  | 1 |  | 10 |  | 0 | 0.65 | 0.65 | Shutdown for branch cutting
2024-12-23 |  |  | 1 | 45 |  |  | 3.5806 | 0 | 3.5806 | Grid Faults
2024-12-24 |  |  | 1 | 10 |  |  | 0.82517 | 0 | 0.82517 | Grid Faults
2024-12-25 | [6 empty] | 0 | 0 | 0
2024-12-26 | [6 empty] | 0 | 0 | 0
2024-12-27 | [6 empty] | 0 | 0 | 0
2024-12-28 |  |  | 1 |  | 6 |  | 0 | 0.39 | 0.39 | Water level sensor power issue
2024-12-29 | [6 empty] | 0 | 0 | 0
2024-12-30 |  |  | 1 | 37 |  |  | 2.8745 | 0 | 2.8745 | Grid Faults
2024-12-31 | [6 empty] | 0 | 0 | 0
2025-01-01 | [6 empty] | 0 | 0 | 0
2025-01-02 | [6 empty] | 0 | 0 | 0
2025-01-03 | [6 empty] | 0 | 0 | 0
2025-01-04 | [6 empty] | 0 | 0 | 0
2025-01-05 | [6 empty] | 0 | 0 | 0
2025-01-06 | [6 empty] | 0 | 0 | 0
2025-01-07 |  |  | 1 | 86 |  |  | 6.2245 | 0 | 6.2245 | 132 kV line repair works
2025-01-08 |  |  | 1 | 75 |  |  | 5.3846 | 0 | 5.3846 | 133 kV line repair works
2025-01-09 | [6 empty] | 0 | 0 | 0
2025-01-10 | [6 empty] | 0 | 0 | 0
2025-01-11 | [6 empty] | 0 | 0 | 0
2025-01-12 | [6 empty] | 0 | 0 | 0
2025-01-13 | [6 empty] | 0 | 0 | 0
2025-01-14 | [6 empty] | 0 | 0 | 0
2025-01-15 | [6 empty] | 0 | 0 | 0
2025-01-16 | [6 empty] | 0 | 0 | 0
2025-01-17 | [6 empty] | 0 | 0 | 0
2025-01-18 | [6 empty] | 0 | 0 | 0
2025-01-19 | [6 empty] | 0 | 0 | 0
2025-01-20 | [6 empty] | 0 | 0 | 0
2025-01-21 | [6 empty] | 0 | 0 | 0
2025-01-22 |  |  | 1 |  | 150 | 150 | 0 | 19.5 | 19.5 | Shutdown for expansion joint repair at AB14
2025-01-23 |  |  | 1 |  | 462 | 462 | 0 | 60.06 | 60.06 | Shutdown for expansion joint repair at AB15
2025-01-24 | [6 empty] | 0 | 0 | 0
2025-01-25 | [6 empty] | 0 | 0 | 0
2025-01-26 | [6 empty] | 0 | 0 | 0
2025-01-27 | [6 empty] | 0 | 0 | 0
2025-01-28 |  |  | 1 |  | 258 | 258 | 0 | 33.54 | 33.54 | 33 kV trip due to branch fall near Bitule
2025-01-29 |  |  | 1 |  | 138 | 138 | 0 | 17.94 | 17.94 | 34 kV trip due to branch fall near Bitule
2025-01-30 |  |  | 1 | 5 |  |  | 0.30662 | 0 | 0.30662 | Grid Faults
2025-01-31 | [6 empty] | 0 | 0 | 0
2025-02-01 | [6 empty] | 0 | 0 | 0
2025-02-02 | [6 empty] | 0 | 0 | 0
2025-02-03 | [6 empty] | 0 | 0 | 0
2025-02-04 |  |  | 1 | 5 |  |  | 0.30313 | 0 | 0.30313 | Grid Faults
2025-02-05 | [6 empty] | 0 | 0 | 0
2025-02-06 | [6 empty] | 0 | 0 | 0
2025-02-07 | [6 empty] | 0 | 0 | 0
2025-02-08 | [6 empty] | 0 | 0 | 0
2025-02-09 | [6 empty] | 0 | 0 | 0
2025-02-10 | [6 empty] | 0 | 0 | 0
2025-02-11 | [6 empty] | 0 | 0 | 0
2025-02-12 | [6 empty] | 0 | 0 | 0
2025-02-13 | [6 empty] | 0 | 0 | 0
2025-02-14 | [6 empty] | 0 | 0 | 0
2025-02-15 | [6 empty] | 0 | 0 | 0
2025-02-16 | [6 empty] | 0 | 0 | 0
2025-02-17 |  |  | 1 |  | 4 | 4 | 0 | 0.52 | 0.52 | Water level Sensor Issue
2025-02-18 | [6 empty] | 0 | 0 | 0
2025-02-19 | [6 empty] | 0 | 0 | 0
2025-02-20 | [6 empty] | 0 | 0 | 0
2025-02-21 | [6 empty] | 0 | 0 | 0
2025-02-22 | [6 empty] | 0 | 0 | 0
2025-02-23 | [6 empty] | 0 | 0 | 0
2025-02-24 | [6 empty] | 0 | 0 | 0
2025-02-25 | [6 empty] | 0 | 0 | 0
2025-02-26 | [6 empty] | 0 | 0 | 0
2025-02-27 | [6 empty] | 0 | 0 | 0
2025-02-28 | [6 empty] | 0 | 0 | 0
2025-03-01 |  |  | 1 | 34 |  |  | 2.0555 | 0 | 2.0555 | Grid Faults
2025-03-02 | [6 empty] | 0 | 0 | 0
2025-03-03 |  |  | 1 | 13 |  |  | 0.83812 | 0 | 0.83812 | Grid Faults
2025-03-04 | [6 empty] | 0 | 0 | 0
2025-03-05 |  |  | 1 | 30 |  |  | 1.8936 | 0 | 1.8936 | Grid Faults (Issue in 33kv line of Balanch NEA line)
2025-03-06 | [6 empty] | 0 | 0 | 0
2025-03-07 | [6 empty] | 0 | 0 | 0
2025-03-08 | [6 empty] | 0 | 0 | 0
2025-03-09 | [6 empty] | 0 | 0 | 0
2025-03-10 | [6 empty] | 0 | 0 | 0
2025-03-11 | [6 empty] | 0 | 0 | 0
2025-03-12 |  |  | 1 | 7 |  |  | 0.58618 | 0 | 0.58618 | Grid faults
2025-03-13 | [6 empty] | 0 | 0 | 0
2025-03-14 | [6 empty] | 0 | 0 | 0
2025-03-15 |  |  | 1 | 14 |  |  | 1.0799 | 0 | 1.0799 | Grid Faults
2025-03-16 | [6 empty] | 0 | 0 | 0
2025-03-17 |  |  | 1 | 28 |  |  | 1.8442 | 0 | 1.8442 | Grid Faults
2025-03-18 | [6 empty] | 0 | 0 | 0
2025-03-19 | [6 empty] | 0 | 0 | 0
2025-03-20 |  |  | 1 |  | 4 | 4 | 0 | 0.52 | 0.52 | Repair works in dam control room
2025-03-21 | [6 empty] | 0 | 0 | 0
2025-03-22 | [6 empty] | 0 | 0 | 0
2025-03-23 |  |  | 1 | 18 |  |  | 1.1899 | 0 | 1.1899 | Grid Faults
2025-03-24 | [6 empty] | 0 | 0 | 0
2025-03-25 | [6 empty] | 0 | 0 | 0
2025-03-26 | [6 empty] | 0 | 0 | 0
2025-03-27 | [6 empty] | 0 | 0 | 0
2025-03-28 | [6 empty] | 0 | 0 | 0
2025-03-29 | [6 empty] | 0 | 0 | 0
2025-03-30 | [6 empty] | 0 | 0 | 0
2025-03-31 | [6 empty] | 0 | 0 | 0
2025-04-01 | [6 empty] | 0 | 0 | 0
2025-04-02 | [6 empty] | 0 | 0 | 0
2025-04-03 | [6 empty] | 0 | 0 | 0
2025-04-04 | [6 empty] | 0 | 0 | 0
2025-04-05 | [6 empty] | 0 | 0 | 0
2025-04-06 | [6 empty] | 0 | 0 | 0
2025-04-07 | [6 empty] | 0 | 0 | 0
2025-04-08 | [6 empty] | 0 | 0 | 0
2025-04-09 | [6 empty] | 0 | 0 | 0
2025-04-10 |  |  | 4 | 14 |  |  | 1.777 | 0 | 1.777 | Grid Faults
2025-04-11 | [6 empty] | 0 | 0 | 0
2025-04-12 |  |  | 2 |  | 5 | 5 | 0 | 0.65 | 0.65 | Issue in 33 kv line
2025-04-13 | [6 empty] | 0 | 0 | 0
2025-04-14 | [6 empty] | 0 | 0 | 0
2025-04-15 | [6 empty] | 0 | 0 | 0
2025-04-16 | [6 empty] | 0 | 0 | 0
2025-04-17 |  |  | 3 | 26 |  |  | 4.1004 | 0 | 4.1004 | Grid faults
2025-04-18 |  |  | 1 |  | 12 | 12 | 0 | 1.56 | 1.56 | DDLO issue
2025-04-19 | [6 empty] | 0 | 0 | 0
2025-04-20 | [6 empty] | 0 | 0 | 0
2025-04-21 | [6 empty] | 0 | 0 | 0
2025-04-22 |  |  | 1 | 2 |  |  | 0.32823 | 0 | 0.32823 | Grid faults
2025-04-23 | [6 empty] | 0 | 0 | 0
2025-04-24 | [6 empty] | 0 | 0 | 0
2025-04-25 | [6 empty] | 0 | 0 | 0
2025-04-26 | [6 empty] | 0 | 0 | 0
2025-04-27 |  |  | 1 | 8 |  |  | 0.99999 | 0 | 0.99999 | Grid faults
2025-04-28 | [6 empty] | 0 | 0 | 0
2025-04-29 | [6 empty] | 0 | 0 | 0
2025-04-30 | [6 empty] | 0 | 0 | 0
2025-05-01 | [6 empty] | 0 | 0 | 0
2025-05-02 | [6 empty] | 0 | 0 | 0
2025-05-03 | [6 empty] | 0 | 0 | 0
2025-05-04 | [6 empty] | 0 | 0 | 0
2025-05-05 | [6 empty] | 0 | 0 | 0
2025-05-06 | [6 empty] | 0 | 0 | 0
2025-05-07 | [6 empty] | 0 | 0 | 0
2025-05-08 | [6 empty] | 0 | 0 | 0
2025-05-09 |  |  | 2 | 45 |  |  | 5.3225 | 0 | 5.3225 | Grid faults
2025-05-10 | [6 empty] | 0 | 0 | 0
2025-05-11 |  |  | 1 | 11 |  |  | 1.3625 | 0 | 1.3625 | Grid faults
2025-05-12 | [6 empty] | 0 | 0 | 0
2025-05-13 | [6 empty] | 0 | 0 | 0
2025-05-14 | [6 empty] | 0 | 0 | 0
2025-05-15 | [6 empty] | 0 | 0 | 0
2025-05-16 |  |  | 1 | 5 |  |  | 0.72125 | 0 | 0.72125 | Grid Faults
2025-05-17 | [6 empty] | 0 | 0 | 0
2025-05-18 | [6 empty] | 0 | 0 | 0
2025-05-19 | [6 empty] | 0 | 0 | 0
2025-05-20 |  |  | 1 | 5 |  |  | 0.80836 | 0 | 0.80836 | Grid Faults
2025-05-21 | [6 empty] | 0 | 0 | 0
2025-05-22 | [6 empty] | 0 | 0 | 0
2025-05-23 | [6 empty] | 0 | 0 | 0
2025-05-24 |  |  | 1 | 5 |  |  | 0.77003 | 0 | 0.77003 | Grid Faults
2025-05-25 | [6 empty] | 0 | 0 | 0
2025-05-26 |  |  | 1 | 10 |  |  | 1.4266 | 0 | 1.4266 | 132 kv earth fault at our side
2025-05-27 |  |  | 2 | 10 |  |  | 1.5385 | 0 | 1.5385 | Grid Faults
2025-05-28 |  |  | 1 |  | 7 | 7 | 0 | 0.91 | 0.91 | Shutdown for BVD test at Balanch
2025-05-29 | [6 empty] | 0 | 0 | 0
2025-05-30 | [6 empty] | 0 | 0 | 0
2025-05-31 |  |  | 1 | 5 |  |  | 0.74912 | 0 | 0.74912 | Grid Faults
2025-06-01 |  |  | 6 | 57 | 23 | 23 | 9.0948 | 2.99 | 12.0848 | Grid Faults + shutdown for BDV Test
2025-06-02 | [6 empty] | 0 | 0 | 0
2025-06-03 |  |  | 3 | 20 |  |  | 2.7324 | 0 | 2.7324 | Grid Faults
2025-06-04 | [6 empty] | 0 | 0 | 0
2025-06-05 | [6 empty] | 0 | 0 | 0
2025-06-06 | [6 empty] | 0 | 0 | 0
2025-06-07 | [6 empty] | 0 | 0 | 0
2025-06-08 |  |  | 1 | 5 |  |  | 0.75609 | 0 | 0.75609 | Grid Faults
2025-06-09 | [6 empty] | 0 | 0 | 0
2025-06-10 | [6 empty] | 0 | 0 | 0
2025-06-11 | [6 empty] | 0 | 0 | 0
2025-06-12 |  |  | 1 | 41 |  |  | 5.451 | 0 | 5.451 | Grid Faults
2025-06-13 |  |  | 2 | 6 |  |  | 0.78661 | 0 | 0.78661 | Grid Faults
2025-06-14 |  |  | 1 | 5 |  |  | 0.81184 | 0 | 0.81184 | Grid Faults
2025-06-15 | [6 empty] | 0 | 0 | 0
2025-06-16 | [6 empty] | 0 | 0 | 0
2025-06-17 | [6 empty] | 0 | 0 | 0
2025-06-18 | [6 empty] | 0 | 0 | 0
2025-06-19 | [6 empty] | 0 | 0 | 0 | Dispatch Instruction by LDC to 7 MW
2025-06-20 | [5 empty] | 600 | 0 | 39 | 39 | Issue in Spear valve sensor of Unit 2 + Dispatch instruction by LDC to 8 MW
2025-06-21 | [5 empty] | 5 | 0 | 0.325 | 0.325 | Unit II shutdown for pressure control of MIV
2025-06-22 | [6 empty] | 0 | 0 | 0
2025-06-23 | [6 empty] | 0 | 0 | 0
2025-06-24 | [6 empty] | 0 | 0 | 0
2025-06-25 |  |  | 1 | 52 |  |  | 9.0662 | 0 | 9.0662 | Grid Faults
2025-06-26 | 0.60692 | 23 |  |  |  |  | 0 | 0 | 0 | Dispatch Instruction by LDC to 9 MW
2025-06-27 | 0 | [5 empty] | 0 | 0 | 0
2025-06-28 | 0 | [5 empty] | 0 | 0 | 0
2025-06-29 | 0 |  | 1 | 11 |  |  | 1.9244 | 0 | 1.9244 | Grid Faults
2025-06-30 | 0 | [5 empty] | 0 | 0 | 0
2025-07-01 | 0 | [5 empty] | 0 | 0 | 0
2025-07-02 | 1.3194 | 50 |  |  |  |  | 0 | 0 | 0 | Dispatch Instruction by LDC to 9 MW
2025-07-03 | 0.58053 | 22 |  |  |  |  | 0 | 0 | 0 | Dispatch Instruction by LDC to 9 MW
2025-07-04 | 0 |  | 1 | 12 |  |  | 2.1008 | 0 | 2.1008 | Grid Faults
2025-07-05 | 0 | [5 empty] | 0 | 0 | 0
2025-07-06 | 0 |  | 1 | 3 |  |  | 0.51565 | 0 | 0.51565 | Grid Faults
2025-07-07 | 0 | [5 empty] | 0 | 0 | 0
2025-07-08 | 5.3831 | 204 |  |  |  |  | 0 | 0 | 0 | Dispatch Instruction by LDC to 9 MW
2025-07-09 | 0 | [5 empty] | 0 | 0 | 0
2025-07-10 | 1.5833 | 60 |  |  |  |  | 0 | 0 | 0 | Dispatch Instruction by LDC to 9 MW
2025-07-11 | 1.5789 | 60 |  |  |  |  | 0 | 0 | 0 | Dispatch Instruction by LDC to 9 MW
2025-07-12 | 0 |  | 1 | 19 |  |  | 3.316 | 0 | 3.316 | Grid Faults
2025-07-13 | 0 | [5 empty] | 0 | 0 | 0 | Power lowered as our generation energy is at higher side
2025-07-14 | 0 |  | 1 |  | 60 | 119 | 0 | 11.635 | 11.635 | Power lowered as our generation energy is at higher side + Shutdown for mothly maintenance
2025-07-15 | 0 | [5 empty] | 0 | 0 | 0 | Power lowered as our generation energy is at higher side
2025-07-16 | 0 | [5 empty] | 0 | 0 | 0 | Power lowered as our generation energy is at higher side
2025-07-17 | 0 |  | 1 |  | 60 | 60 | 0 | 7.8 | 7.8 | Power lowered as our generation energy is at higher side + Shutdown for turbine checking
2025-07-18 | 10.65 | 336 |  |  |  |  | 0 | 0 | 0 | Dispatch instruction by LDC for decreasing power to 9 MW for 33 min and then to 8 MW
2025-07-19 |  |  | 1 | 20 |  |  | 3.4788 | 0 | 3.4788 | Grid Faults
2025-07-20 | 9 | 180 |  |  |  |  | 0 | 0 | 0 | Dispatch instruction by LDC for decreasing power to 9 MW for 180 min
2025-07-21 | 0 | [5 empty] | 0 | 0 | 0
2025-07-22 | 6.65 | 133 | 1 | 4 |  |  | 0.67688 | 0 | 0.67688 | Dispatch instruction by LDC for decreasing power to 7 MW for 133 min + Grid Faults
2025-07-23 | 1.9667 | 118 | 1 | 4 |  |  | 0.69916 | 0 | 0.69916 | Dispatch instruction by LDC for decreasing power to 9 MW for 118 min
2025-07-24 | 0 | [5 empty] | 0 | 0 | 0
2025-07-25 | 0 | [5 empty] | 0 | 0 | 0
2025-07-26 | 0.71667 | 43 |  |  |  |  | 0 | 0 | 0 | Dispatch instruction by LDC for decreasing power to 9 MW
2025-07-27 | 0 |  | 1 |  | 7 | 70 | 0 | 6.7375 | 6.7375 | Shutdown of plant due to heavy flood in dam and blockage in trashrack
2025-07-28 | 0 |  | 1 | 4 |  |  | 0.69916 | 0 | 0.69916 | Grid Faults
2025-07-29 | 0 | [5 empty] | 0 | 0 | 0
2025-07-30 | 0 | [5 empty] | 0 | 0 | 0
2025-07-31 | 0 | [5 empty] | 0 | 0 | 0
2025-08-01 | 0 | [5 empty] | 0 | 0 | 0
2025-08-02 | 0 | [5 empty] | 0 | 0 | 0
2025-08-03 | 0 |  | 1 |  |  | 15 | 0 | 1.3125 | 1.3125 | Shutdown of plant due to heavy flood in dam and blockage in trashrack
2025-08-04 | 0 |  | 1 |  | 5 | 5 | 0 | 0.875 | 0.875 | Shutdown for tree cutting
2025-08-05 | 7.2 | 237 | 4 | 18 |  |  | 3.0506 | 0 | 3.0506 | Grid faults and LDC dispatch instruction
2025-08-06 |  |  | 3 | 17 |  |  | 2.9627 | 0 | 2.9627 | Grid faults
2025-08-07 | 17.1667 | 206 | 1 | 34 |  |  | 5.7311 | 0 | 5.7311 | Grid faults and LDC dispatch instruction
2025-08-08 | [6 empty] | 0 | 0 | 0
2025-08-09 | 6.1 | 366 |  |  |  |  | 0 | 0 | 0
2025-08-10 | 0 | [5 empty] | 0 | 0 | 0
2025-08-11 | 0 | [5 empty] | 0 | 0 | 0
2025-08-12 | 1.0333 | 62 |  |  |  |  | 0 | 0 | 0 | Dispatch instruction by LDC for decreasing power to 9 MW
2025-08-13 | 0 |  | 3 | 17 | 31 | 67 | 2.9323 | 8.575 | 11.5073 | Grid Faults+ shutdown plant for maintenance works
2025-08-14 | 0 |  | 1 |  | 948 | 948 | 0 | 165.9 | 165.9 | Two phase of transmission line damaged by rockfall at Bitule
2025-08-15 | 0 |  | 1 |  | 480 | 480 | 0 | 84 | 84 | Two phase of transmission line damaged by rockfall at Bitule
2025-08-16 | 0 | [5 empty] | 0 | 0 | 0
2025-08-17 | 0 |  | 1 |  |  | 5 | 0 | 0.4375 | 0.4375 | Shutdown of Unit II due to high pressure in MIV tank